## Slide 1: Comparison of the Risks associated with Natural Gas and Hydrogen Distribution Networks
Hazards 32, 18th to 20th October 2022
Andy Phillips, Principal Engineer, DNV
Notes: Duration of around 20 minutes

## Slide 2: Introduction
This work has been conducted by DNV as part of Phase 2 of the UK Gas Distribution Networks and Ofgem National Innovation Competition funded H21 project.
Authors of accompanying paper:
  Andrew Phillips and Ann Halford (DNV)
  Russ Oxley (Northern Gas Networks)
Thank you to
  Northern Gas Networks
  HSE Science and Research Centre

## Slide 3: Contents
Overview of H21 project
Description of CONIFER
Differences between natural gas and hydrogen distribution systems
Example calculations

## Slide 4: H21 Project, Phase 1
Phase 1A – Background testing
  Carried out by HSE Science Division
  Investigation of the leakage rate of distribution network assets
  Included experimental testing of methane and hydrogen
Phase 1B – Consequence testing
  Carried out by DNV
  Included large experimental programme at our Spadeadam test facility
  Development of a QRA model
    Only mains and services upstream of the ECV

## Slide 5: Phase 1B Experimental Programme
‘Small’ releases underground
  Investigate outflow and migration through the ground
‘Large’ releases
  Investigate ground breaking and fire severity
Ignition potential tests
  Domestic appliances and common equipment
Explosion tests in a variety of enclosures
  Meter box, kiosks etc.
Operational safety tests and demonstrations

## Slide 6: H21 Project, Phase 2
Inclusion of releases downstream of the ECV
  Meter
  Pipework
  Appliances
Model developments
  Hydrogen explosion model
  Hole size distributions
  Benchmarking against historical data
  Overpressure effects outside buildings
  Many minor improvements

## Slide 7: The CONIFER Package
Includes releases from
  Mains
  Services
  Downstream of ECV (meter, pipework, appliances)
Hazards modelled include
  Fires outdoors
  Explosions in buildings
  Generation of overpressure from delayed ignition in the open
Detailed enough to quantify risks from
  Different gases
  Different design options
  Different building types

## Slide 8: Structure of CONIFER
Notes: Not discussed in detail, just to give an idea of the number of steps involved and the complexity

## Slide 9: Risk Predictions for Great Britain
Risk comparison for natural gas and hydrogen networks
Based on
  Detailed data from NGN’s network
  High level data from all networks (to scale up the results)
  Public data for house sizes and populations etc.
Many combinations of main, service and building considered
  Pipe material, pressure and diameter
  Building type, occupancy pattern and proximity to main
  274,000 combinations of main type, building type and separation distance
  62,000 combinations of service type and building type
  980 combinations of building configuration for releases downstream of ECV

## Slide 10: Benchmarking Natural Gas Results for Great Britain
Release Source | Category | Number per year | 
 |  | Historical | Predicted
Main | Explosions | 1.0 to 3.1 | 4.8 total, 2.2 over 70 mbar
 | Fatalities | 0.3 to 0.5 | 0.5
 | Injuries | 2.5 to 3.0 | 0.9 serious, 1.0 minor, 1.8 total
Service | Explosions | 0.5 to 1.5 | 2.6 total, 1.1 over 70 mbar
 | Fatalities | 0.1 to 0.3 | 0.2
 | Injuries | 1.0 to 2.0 | 0.5 serious, 0.5 minor, 1.0 total
Downstream of the ECV | Explosions | 4.0 to 6.5 | 22.1 total, 9.4 over 70 mbar
 | Fatalities | 0.5 to 1.8 | 1.7
 | Injuries | 4.0 to 11.0 | 3.8 serious, 4.3 minor, 8.1 total

## Slide 11: Comparison between Natural Gas and Hydrogen
Similarities
Release frequencies
Differences
Volumetric outflow rate higher for H2
Above ground dispersion further
Flammable concentration range (similar LFL but much higher UFL for H2)
Ignition probability higher for hydrogen
Explosion consequences could be worse for hydrogen
Detonation possible
Effects outside source building
Unconfined explosions in open air
Hydrogen does not produce CO
Below ground dispersion behaviour
Fire severity
Human behaviour, response to leaks

## Slide 12: Hydrogen Explosions
Explosions dominate the risk for most mains (natural gas or hydrogen)
Unconfined explosions in open air possible
Explosion develops more quickly
Detonation possible
More likely to cause fatalities outdoors and in other buildings
Overpressure dependent on concentration
Example room, stoichiometric mixture
Notes: Fires dominate for transmission pipelines, rather than explosions
Unconfined VCEs are not considered for natural gas and historically not an issue
Speed of explosion development doesn’t allow vents and walls to fail in same way as natural gas
New Ferry incident shows the sort of damage that we need to prevent (more severe than natural gas)

## Slide 13: Example of Explosion Effects
Explosion occurs in yellow ‘Event House’
Semi-detached adjoining neighbour
Also affects
  Next door neighbour
  Houses across the road
  Houses at bottom of garden
Risk calculation includes
  Explosion effects in the Event House and neighbour
  Blast wave impacting other buildings
  Direct overpressure effects
  Glass and bricks ejected into street

## Slide 14: Example Explosion Effects
Credible leak is a 0.3 mm gap around a 22 mm pipe
Natural gas gives 0.90 m3/hour and 9.0% concentration
Hydrogen gives 1.45 m3/hour and 7.2% concentration
Explosion Example |  | Predicted Fatalities |  |  |  |  | 
 |  | Event House |  | All Other Houses |  | Total | 
 |  | Indoors | In Gardens | Indoors | In Gardens | Average | Range
Worst case | Natural gas | 0.27 | < 0.01 | 0.10 | < 0.01 | 0.37 | 0.19 to 0.56
 | Hydrogen | 0.96 | 0.02 | 1.43 | 0.03 | 2.44 | 1.30 to 3.67
Credible leak | Natural gas | 0.10 | < 0.01 | 0 | < 0.01 | 0.10 | 0.05 to 0.15
 | Hydrogen | 0.06 | 0 | 0 | 0 | 0.05 | 0.03 to 0.08

## Slide 15: Carbon Monoxide
RIDGAS data from HSE
Downward trend in fatalities
Significant contribution to natural gas risk
  Around 2.5 fatalities per year from fires and explosions (with variation)
  Similar number or more from CO poisoning
  Many more injuries from CO poisoning
Clear safety benefit for hydrogen

## Slide 16: Conclusions
Risk assessment methodology for distribution has been developed
  CONIFER package
  Experimental validation from H21, previous work and public data
  Gives realistic predictions of natural gas risks
  Allows quantification of all risk sources up to 7 barg
Differences between natural gas and hydrogen distribution systems
  Physical properties (hence outflow, gas accumulation etc.)
  Explosions do not behave the same way
  Carbon monoxide eliminated with hydrogen
Notes: Quantification of risk sources allows risk mitigation options to be identified and evaluated
Experience with natural gas can be applied, but there are differences with hydrogen

## Slide 17: Thank you for your attention
Please feel free to contact me
Andy Phillips, Principal Engineer, Safety and Integrity
Andrew.Phillips@dnv.com